## Design Tool
SALINO® 250 Pressure Center ̶ Design Tool
Unit Selection
| Pressure |  |  |  | Membrane | [5 empty] | = required Input
| Flow |  |  |  | Recovery Rate | 30 | %
Temperature
Permeate
[8 empty] | Flow | 4.1667 | m³/h
High Pressure Feed
| Flow | 13.8889 | m³/h |  |  |  |  | Limiting Values for Operation
| Pressure | 65 | bar |  |  |  |  | Minimum feed pressure |  |  | 2.9 | bar
[8 empty] | Minimum operating pressure |  |  | 30 | bar
[8 empty] | Maximum operating pressure |  |  | 70 | bar
[5 empty] | High Pressure Brine |  |  | Minimum back pressure |  |  | 2 | bar
[5 empty] | Flow | 9.7222 | m³/h | Maximum water temperature |  |  | 40 | °C
[5 empty] | Pressure | 64 | bar | Minimum rotational speed |  |  | 600 | rpm
[8 empty] | Maximum rotational speed |  |  | 1750 | rpm
Input
[8 empty] | Permeate Flow |  |  | 100 | m³/day
[8 empty] | Membran pressure drop |  |  | 1 | bar
[8 empty] | Electric drive |  |  | Standard IE3
| Feed Water | [6 empty] | Electrical Motor efficiency |  |  | 90 | %
| Flow | 14.1291 | m³/h |  |  |  |  | Frequency Converter |  |  | Standard
| Pressure | 2.9 | bar |  |  |  |  | Frequency Converter efficiency |  |  | 90 | %
[5 empty] | Low Pressure Brine |  |  | SALINO®
[5 empty] | Flow | 9.5278 | m³/h | SALINO® hydraulic efficiency |  |  | 97 | %
[5 empty] | Pressure | 2 | bar | Number of SALINO®s required |  |  | 1
[8 empty] | Rotational speed |  |  | 1028.8066 | rpm
| Sea Water | [6 empty] | Power savings |  |  | 16.342 | kW
| Salinity | 47000 | ppm |  |  |  |  | Total Lubrication Flow |  |  | 0.43464 | m³/h
| Temperature | 18 | °C |  |  | Warning |  | Energy Data
[6 empty] | - none - |  | Rated Power |  |  | 10.1302 | kW
[8 empty] | Energy costs |  |  | 0.16 | €/kWh
[8 empty] | Energy efficiency |  |  | 2.4313 | kWh/m³
[8 empty] | Specific energy costs |  |  | 0.389 | €/m³
[8 empty] | Energy savings |  |  | 176735.4367 | kWh/a
|  |  |  | www.salinnova.com |  |  | engineered by | CO2 savings |  |  | 106.9249 | t/a
| All calculated data presented does not represent guaranteed performance. | [6 empty] | Energy cost savings |  |  | 28277.6699 | €/a

## Data Sheet (hidden)
SALINO® Pressure Center
Created: | 2018-03-01 |  | for RO-Desalination
SALINO® Design Tool |  |  | Project:
for prior membrane calculation
Limiting Values for Operation
|  | Minimum feed pressure: | 2.872 | bar
|  | Minimum operating pressure: | 30 | bar
|  | Maximum operating pressure: | 70 | bar
|  | Minimum back pressure: | 2 | bar
|  | Maximum water temperature: | 50 | °C
Input from Calculation
|  | Feed TDS: | 47000 | ppm
|  | Overall Recovery: | 30 | %
|  | Permeate Flow: | 4.1667 | m³/h
|  | (Membrane) Feed Pressure: | 65 | bar
|  | Feed Temperature: | 18 | °C
Operating Data (calculated)
|  | Number of SALINO®s required: | 1
|  | Feed water flow: | 14.1291 | m³/h
|  | Brine flow: | 9.5278 | m³/h
|  | Rotational speed: | 1028.8066 | rpm
|  | Membrane Pressure drop: | 1 | bar
|  | Energy costs: | 0.16 | €/kWh
SALINO® Pressure Center
|  | Manufactured in: | Duplex Stainless Steel
|  | Electrical Motor efficiency: | 90 | %
|  | Frequency Converter efficiency: | 90 | %
|  | Rated Power: | 10.1302 | kW
|  | Rated Maximum Power: | 10.9433 | kW
|  | Energy efficiency: | 2.4313 | kWh/m³
|  | CO2 savings: | 106.9249 | t/a
|  | Energy cost savings: | 28277.6699 | €/a
All calculated data presented does not represent guaranteed performance.

## Berechnungen (hidden)
Berechnungen
Input | Recovery Rate | RR | 30 | % |  | gegeben | Volume pump | Vpump | 225 | cm3
| Membrane Feed Pressure | ps | 65 | bar |  |  | mechanical efficiency | ηmech | 97.6 | %
| Maximum operating pressure | ps max | 70 | bar |  |  | volumetric efficiency pump | ηvol pump | 98.3 | %
| Permeate Flow | Qperm | 4.1667 | m3/h |  |  | volumetric efficiency motor | ηvol motor | 98 | %
|  |  | 100 | m3/d |  |  | CO2 equivalent | mCO2/kWh | 0.605 | kg/kWh
| Feed Temperature | Tfeed | 18 | °C
| Feed Salinity | Sfeed | 47000 | ppm
| Membrane Pressure Drop | Δpv | 1 | bar
| Brine discharge pressure | pback | 2 | bar
| Electrical Motor efficiency | ηEM | 90 | %
| Frequency Converter efficiency | ηFU | 90 | %
| Energy Costs | KE | 0.16 | €/kWh
| Front pressure | pfeed lp | 2.9 | bar
= erforderliche Eingabe
[7 empty] | Max. Membrane Pressure ps max | 70 | bar
| Feed High Pressure | Qfeed hp | 13.8889 | m3/h |  |  |  | 13.8889 | m3/h
| Brine High Pressure | Qbrine hp | 9.7222 | m3/h |  |  |  | 9.7222 | m3/h
| Feed Low Pressure | Qfeed lp | 14.1291 | m3/h |  |  |  | 14.1291 | m3/h
| Brine Low Pressure | Qbrine lp | 9.5278 | m3/h |  |  |  | 9.5278 | m3/h
| Total Lubrication Flow | Qlub | 0.43464 | m3/h |  |  |  | 0.43464 | m3/h
| calculated Rotational speed | n | 1028.8066 | rpm |  |  |  | 1028.8066 | rpm
| Rotational speed per SALINO | n | 1028.8066 | rpm |  |  |  | 1028.8066 | rpm
| difference pressure pump | dp | 62.1 | bar |  |  |  | 67.1 | bar
| Brine High Pressure | pbrine hp | 64 | bar |  |  |  | 69 | bar
| Power Pump | Ppump | 24.5475 | kW |  |  |  | 26.5239 | kW
| Volume ERD | VERD | 157.5 | cm3 |  |  |  | 157.5 | cm3
| Power ERD | PERD | 16.342 | kW |  |  |  | 17.6599 | kW
| Power shaft | Pshaft | 8.2055 | kW |  |  |  | 8.864 | kW
| Electrical Power | Pel | 10.1302 | kW |  |  |  | 10.9433 | kW
| Energy efficiency | SECel | 2.4313 | kWh/m3 |  |  |  | 2.6264 | kWh/m3
| specific Energy Costs | KE spec | 0.389 | €/m3 |  |  |  | 0.42022 | €/m3
| Energy savings | Esave el/a | 176735.4367 | kWh/a |  |  |  | 190988.2945 | kWh/a
| CO2 savings | CO2 saving/a | 106.9249 | t/a |  |  |  | 115.5479 | t/a
| Energy cost savings | KE save/a | 28277.6699 | €/a |  |  |  | 30558.1271 | €/a
= wird dem Kunden angezeigt
| angebotene RR | 25 | % | Maximum operating pressure |  |  | Minimum feed pressure f(n) | 2.872 | bar
|  | 26 | % |  | 70 | bar
|  | 27 | % |  | 80 | bar
|  | 28 | % |  | 120 | bar
|  | 29 | % | Anzahl notw. SALINOs |  | 1
|  | 30 | %
|  | 31 | %
|  | 32 | % | Warning | 1
|  | 33 | %
|  | 34 | %
|  | 35 | %
|  | 36 | %
|  | 37 | %
|  | 38 | %
|  | 39 | %
|  | 40 | %
|  | 41 | %
|  | 42 | %
|  | 43 | %
|  | 44 | %
|  | 45 | %
|  | 46 | %
|  | 47 | %
|  | 48 | %
|  | 49 | %
|  | 50 | %
| Motoren | Standard IE3
Non-Standard
bare shaft pump
| FU | Standard
Non-Standard
exclusive

## Units (hidden)
Unit Selection
Umrechnungsfaktoren
pressure | TRUE | 1 | bar | 1
| FALSE | 14.5038 | psi
flow | TRUE | 1 | m³/h | 1
| FALSE | 4.4029 | gpm
temperature | TRUE
FALSE

## Quotation data (hidden)
SALINO® 250 Pressure Center scope of supply
Item | Description | Part no. | Qty. | Unit
00100 | 01602765 |  | 1 | PC
SALINO Pressure Center
Material: Duplex 1.4462
Recovery Rate 30 %
00110 | MAT.-NR. 30 kW Motor |  | 1 | PC
Squirrel-Cage-Motor
Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B)
IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz)
3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD
Frame material: grey cast iron
paint finish resistant to salt-laden air
motor protection 3 PTC thermistors
00120 | 01554711 |  | 1 | PC
Bellhousing PG400
00130 | 01554712 |  | 1 | PC
Flexible Coupling BoWex M-65
00140 | 01553736 |  | 1 | PC
Mountingframe 270x600x1560
00200 | MAT.-NR. Pumpdrive R 30 kW |  | 1 | PC
Frequency Converter PumpDrive R (KSB202)
3AC 380-480 V ±10 % * 50/60 Hz
IP20 * 30 kW * I at 400V=61,0A
Maximum ambient temperature +50°C
Dimensions [mm] H=650 x B=242 x T=260
engineered by

## Identnumbers (hidden)
Recovery Rate | bare shaft pump | PC 14 (22 kW) | PC 20 (30 kW) | PC 23 (37 kW) | Non-Standard
25 | 01548647 | 01700401 | 01602760 | 01704526 | 00025
26 | 01548648 | 01700402 | 01602761 | 01704538 | 00026
27 | 01548649 | 01700403 | 01602762 | 01704539 | 00027
28 | 01548650 | 01700404 | 01602763 | 01704540 | 00028
29 | 01548651 | 01700405 | 01602764 | 01704541 | 00029
30 | 01548652 | 01700406 | 01602765 | 01704542 | 00030
31 | 01548653 | 01700408 | 01602766 | 01704543 | 00031
32 | 01548654 | 01700409 | 01602797 | 01704544 | 00032
33 | 01544220 | 01700410 | 01602798 | 01704545 | 00033
34 | 01548655 | 01700411 | 01602799 | 01704546 | 00034
35 | 01548656 | 01700412 | 01602800 | 01704547 | 00035
36 | 01548657 | 01700413 | 01602801 | 01704548 | 00036
37 | 01548658 | 01700414 | 01602802 | 01704549 | 00037
38 | 01548659 | 01700415 | 01602803 | 01704550 | 00038
39 | 01548660 | 01700416 | 01602804 | 01704551 | 00039
40 | 01544221 | 01700417 | 01602805 | 01704552 | 00040
41 | 01550908 | 01700418 | 01602806 | 01704553 | 00041
42 | 01550909 | 01700419 | 01602807 | 01704554 | 00042
43 | 01550910 | 01700420 | 01602808 | 01704555 | 00043
44 | 01550911 | 01700421 | 01602809 | 01704556 | 00044
45 | 01550912 | 01700422 | 01602810 | 01704557 | 00045
46 | 01550913 | 01700423 | 01602811 | 01704558 | 00046
47 | 01550914 | 01700424 | 01602812 | 01704559 | 00047
48 | 01550915 | 01700425 | 01602813 | 01704560 | 00048
49 | 01550916 | 01700426 | 01602814 | 01704561 | 00049
50 | 01550917 | 01700427 | 01602815 | 01704562 | 00050
Spaltenindex | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| Mat.-Nr. | Motor Mat.-Nr. | Motorbezeichnung | Motordaten Zeile 1 | Motordaten Zeile 2 | Motordaten Zeile 3 | Motordaten Zeile 4 | Motordaten Zeile 5 | Motordaten Zeile 6 | Mat.-Nr. Pumpenträger | Pumpenträgerbezeichnung | Mat.-Nr. Kupplung | Kupplungsbezeichnung | Mat.-Nr. Montagerahmen | Montagerahmenbezeichnung | FU-Mat.-Nr. | FU-Bezeichnung | FU-Daten Zeile 1 | FU-Daten Zeile 2 | FU-Daten Zeile 3 | FU-Daten Zeile 4
barshaft pump | 01548647
01548648
01548649
01548650
01548651
01548652
01548653
01548654
01544220
01548655
01548656
01548657
01548658
01548659
01548660
01544221
01550908
01550909
01550910
01550911
01550912
01550913
01550914
01550915
01550916
01550917
PC 14 | 01700401 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553705 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700402 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553706 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700403 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553707 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700404 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553708 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700405 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553709 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700406 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553710 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700408 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553711 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700409 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553712 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700410 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553713 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700411 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553714 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700412 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553715 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700413 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553716 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700414 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553717 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700415 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553718 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700416 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553719 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700417 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553720 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700418 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553721 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700419 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553722 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700420 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553723 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700421 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553724 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700422 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553725 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700423 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553726 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700424 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553727 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700425 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553728 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700426 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553729 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01700427 | MAT.-NR. 22 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 6pole * BG200L * IMB35 * 22kW (50 Hz) * 26,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553730 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 22 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 22 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
PC 20 | 01602760 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553731 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602761 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553732 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602762 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553733 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602763 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553734 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602764 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553735 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602765 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553736 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602766 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553737 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602797 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553738 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602798 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553739 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602799 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553740 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602800 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553741 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602801 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553742 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602802 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553743 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602803 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553744 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602804 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553745 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602805 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553746 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602806 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553747 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602807 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553748 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602808 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553749 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602809 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553750 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602810 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553751 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602811 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553752 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602812 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553753 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602813 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553754 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602814 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553755 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 01602815 | MAT.-NR. 30 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG200L * IMB35 * 30kW (50 Hz) * 34,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG400 | 01554712 | Flexible Coupling BoWex M-65 | 01553756 | Mountingframe 270x600x1560 | MAT.-NR. Pumpdrive R 30 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 30 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
PC 23 | 01704526 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704538 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704539 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704540 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704541 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704542 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704543 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704544 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704545 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704546 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704547 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704548 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704549 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704550 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704551 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704552 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704553 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704554 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704555 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704556 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704557 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704558 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704559 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704560 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704561 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
| 01704562 | MAT.-NR. 37 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG225S * IMB35 * 37kW (50 Hz) * 42,5kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | MAT.-NR. Pumpenträger PG450 | Bellhousing PG450 | MAT.-NR. BoWex 37 kW | Flexible Coupling BoWex M-65 | MAT.-NR. Montagerahmen 225S | Mountingframe 50x600x1672 | MAT.-NR. Pumpdrive R 37 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 37 kW * I at 400V=73,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=680 x B=308 x T=310
non-standard Motor | 00025 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00026 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00027 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00028 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00029 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00030 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00031 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00032 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00033 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00034 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00035 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00036 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00037 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00038 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00039 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00040 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00041 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00042 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00043 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00044 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00045 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00046 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00047 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00048 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00049 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00050 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
non-standard FU |  | Frequency Converter according to customers specification