## Overview_Salino_cleaned (hidden)
Modellreihen Salinnova
Datum: | 2019-10-15
[8 empty] | Kolben |  |  | Recovery Rates (=Permeat Rate) | [10 empty] | pump speed |  | Zulässige Betriebsbedingunge | [19 empty] | Motor Sizes (Max. Motor: pmax2 at 1.500 RPM at max. RR with 15% make-up Min. Motor: pmax1 at 1.500 RPM und min. RR with 15% make-up)
Model | Remark | Duplex | EL316 | boosted | super boosted | displacement pump | displacement ERD | Piston Design |  |  | 25% | 30% | 35% | 40% | 45% | 50% | 55% | 60% | 65% | 70% | 75% | RPMmin | RPMmax | Fluid Temperatur |  | Salinity | LP in (Feedwater) |  |  |  | HP Out (Osmose Druck) pmax1 : nominal pressure for PN80 Hoses ( 2" und 3") pmax2: maximum pressure for pump unit * plug fitted force feed* |  |  | HP In (Brine) | LP Out |  | Lubrication Lines |  |  | total lubrication Flow= 100%-(100%-X+100%-Y) |  |  | approx. Motor efficiency | make-up on calculated motor sizing (torque) | 80M-4 | 90S-4 | 90L-4 | 90L-4V* | 100L-4 | 112M-4 | 132S-4 | 132M-4 | 160M-4 | 160L-4 | 180M-4 | 180L-4 | 200L-4K | 225S-4 | 225M-4 | 250M-4 | 280S-4 | 280M-4K | 315S-4 | 315M-4 | 315L-4K | 315L-4M | 315L-4L* | 315L-4V* | shaft pump-side |  |  | Gleitringdichtung (=mechanical seal) | pump connections
[6 empty] | ccm/rev | ccm/rev | Number | diameter | strocke | [13 empty] | Tmin | Tmax |  | Formel: min.pressure kidney*(1+mark-up)+(factor a*(design RPMs/min. RPMs)^2) |  |  | pmax | pmin | pmax1 | pmax2 | as HP Out | pmin | pmax | pmax | mechanical efficiency pump | mechanical efficiency ERD | volumetric efficiency pump side | volumetric efficiency ERD side | efficiency VFD |  | pmax | 0.75 | 1.1 | 1.5 | 2.5 | 3 | 4 | 5.5 | 7.5 | 11 | 15 | 18.5 | 22 | 30 | 37 | 45 | 55 | 75 | 90 | 110 | 132 | 160 | 200 | 250 | 315 | D | L | Form | S: Standard O: optional R: ohne GLRD (Dichtring) | LP in | HP out | HP in | LP out | Lubrication Pump | Lubrication ERD | Hoses HP1 | Hoses HP2 | Hoses LP | CPV | Sensor 1 | Sensor 2 | max torque
Salino | [43 empty] | IE3-Motor: | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | [10 empty] | 80 | 120
[8 empty] | Stk. | mm | mm | [13 empty] | °C | °C | max. ppm | Faktor a | min pressure in Kidney | mark-up warning level | bar | bar | bar | bar | [10 empty] | shaft motor side | [24 empty] | mm | mm | N: key Z: toothed | [13 empty] | Nm
bar
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86
5 |  | x |  |  |  | 6 | 3 | 5 |  |  | 25% |  | 35% | [8 empty] | 600 | 1750 | 2 | 50 | 50000 | 0.12 | 2.5 | 10% |  | 20 | 80 | 120 | wie HP Out | 2 | 4 | 0.75 | 91% | 91% | 90% | 90% | 94% | 84% | 20% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | 34 | 8.98 | N | S | G 3/8" | G 3/8" | G 3/8" | G 3/8" | G 1/4" | G 1/4" | [5 empty] | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 12.7
60RR25 | P60M30 | x |  |  |  | 51 | 35 |  |  |  | 25% | [10 empty] | 600 | 1750 | 2 | 50 | 50000 | 0.12 | 2.5 | 10% |  | 20 | 80 | 120 | wie HP Out | 2 | 4 | 0.75 | 92% | 92% | 97% | 96% | 96% | 89% | 15% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | DR: 63 GLRD: 88 | 27.98 | N | S | G 1" | G 1" | G 3/4" | G 3/4" | G 1/2" | G 1/2" | [5 empty] | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 169.8
60RR30 | P51M30 | x |  |  |  | 51 | 30 |  |  |  |  | 30% | [9 empty] | 600 | 1750 | 2 | 50 | 50000 | 0.12 | 2.5 | 10% |  | 20 | 80 | 120 | wie HP Out | 2 | 4 | 0.75 | 92% | 92% | 97% | 96% | 96% | 89% | 15% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | DR: 63 GLRD: 88 | 27.98 | N | S | G 1" | G 1" | G 3/4" | G 3/4" | G 1/2" | G 1/2" | [5 empty] | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 169.8
60RR35 | P63M30 | x |  |  |  | 63 | 35 | [5 empty] | 35% | [8 empty] | 600 | 1750 | 2 | 50 | 50000 | 0.12 | 2.5 | 10% |  | 20 | 80 | 120 | wie HP Out | 2 | 4 | 0.75 | 92% | 92% | 97% | 96% | 96% | 89% | 15% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | DR: 63 GLRD: 88 | 27.98 | N | S | G 1" | G 1" | G 3/4" | G 3/4" | G 1/2" | G 1/2" | [5 empty] | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 169.8
60RR40 | P63M35 | x |  |  |  | 63 | 30 | [6 empty] | 40% | [7 empty] | 600 | 1750 | 2 | 50 | 50000 | 0.12 | 2.5 | 10% |  | 20 | 80 | 120 | wie HP Out | 2 | 4 | 0.75 | 92% | 92% | 97% | 96% | 96% | 89% | 15% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | DR: 63 GLRD: 88 | 27.98 | N | S | G 1" | G 1" | G 3/4" | G 3/4" | G 1/2" | G 1/2" | [5 empty] | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 169.8
60RR50 | P63M30 | x |  |  |  | 80 | 33 | [8 empty] | 50% | [5 empty] | 600 | 1750 | 2 | 50 | 50000 | 0.12 | 2.5 | 10% |  | 20 | 80 | 120 | wie HP Out | 2 | 4 | 0.75 | 92% | 92% | 97% | 96% | 96% | 89% | 15% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | DR: 63 GLRD: 88 | 27.98 | N | S | G 1" | G 1" | G 3/4" | G 3/4" | G 1/2" | G 1/2" | [5 empty] | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 169.8
60RR45 | P70M35 | x |  |  |  | 70 | 35 | [7 empty] | 45% | [6 empty] | 600 | 1750 | 2 | 50 | 50000 | 0.12 | 2.5 | 10% |  | 20 | 80 | 120 | wie HP Out | 2 | 4 | 0.75 | 92% | 92% | 97% | 96% | 96% | 89% | 15% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | DR: 63 GLRD: 88 | 27.98 | N | S | G 1" | G 1" | G 3/4" | G 3/4" | G 1/2" | G 1/2" | [5 empty] | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 169.8
60RR55 | P80M35 | x |  |  |  | 80 | 35 | [9 empty] | 55% |  |  |  |  | 600 | 1750 | 2 | 50 | 50000 | 0.12 | 2.5 | 10% |  | 20 | 80 | 120 | wie HP Out | 2 | 4 | 0.75 | 92% | 92% | 97% | 96% | 96% | 89% | 15% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | DR: 63 GLRD: 88 | 27.98 | N | S | G 1" | G 1" | G 3/4" | G 3/4" | G 1/2" | G 1/2" | [5 empty] | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 169.8
120/183ccm |  | x |  |  |  | 183 |  | 9 | 32 | 24.9401 |  | 30% | 35% | 40% | 45% | [6 empty] | 500 | 1750 | 2 | 50 | 50000 | 0.15 | 2.8 | 10% |  | 20 | 80 | 120 | wie HP Out | 2.5 | 4 | 0.75 | 96% | 96% | 95% | 95% | 97% | 90% | 12% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | 13 Zähne | 88.5 | Z | S | SAE 2" | SAE 2" | SAE 2" | SAE 2" | G 3/4" | G 3/4" | [5 empty] | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 605.8
250 |  | x |  |  |  | 225 |  | 9 | 32 | 30.6641 | 25% | 30% | 35% | 40% | 45% | 50% | 55% |  |  |  |  | 600 | 1750 | 2 | 50 | 50000 | 0.15 | 3 | 10% |  | 20 | 80 | 120 | wie HP Out | 2.5 | 4 | 0.75 | 96% | 96% | 97% | 96% | 97% | 93% | 12% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | 13 Zähne | 88.5 | Z | S | SAE 2" | SAE 2" | SAE 2" | SAE 2" | G 3/4" | G 3/4" | [5 empty] | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 605.8
250+E |  | x |  |  |  | 286 |  |  |  |  | 25% | 30% | 35% | 40% | 45% | 50% | 55% |  |  |  |  | 600 | 1650 | 2 | 50 | 50000 | 0.15 | 3.5 | 10% |  | 20 | 80 | 120 | wie HP Out | 2.5 | 4 | 0.75 | 96% | 96% | 97% | 96% | 97% | 93% | 12% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% |  |  | Z | S | SAE 2" | SAE 2" | SAE 2" | SAE 2" | G 3/4" | G 3/4" |  |  |  |  | 1 pc Pressure switche PP; digital output for inlet pressure monitoring (SAL9399 250E/500E LP in) | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 605.8
500E |  | x |  |  |  | 625 |  | 9 | 45 | 43.0727 | 25% | 30% | 35% | 40% | 45% | 50% | 55% |  |  |  |  | 600 | 1500 | 2 | 50 | 50000 | 0.15 | 3.5 | 10% |  | 20 | 80 | 80 | wie HP Out | 2.5 | 4 | 0.75 | 96% | 96% | 97% | 96% | 98% | 94% | 10% | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95% | 57.98 | 114 | N | S | 3" SAE | 3" SAE | 3" SAE | 3" SAE | G 1" | G 1" | 2 pcs. High pressure flexible hose PHD250 X 1500 SF90VA VIC2"VA; max. operating pressure: 80bar/ 1.150psi; incl. SAE-Adapter 3" to 2" (SAL8025 500E HP in/out) | 2 pcs. High pressure flexible hose PHD250 X 1500 SF90VA VIC2"VA; max. operating pressure: 160bar/ 2.300psi; incl. SAE-Adapter 3" to 2" (SAL8XXX 500E HHP in/out) | 2 pcs. High pressure flexible hose PHD276 X 1500 SF90VA VIC3"VA; max. operating pressure: 63bar/ 950psi; " (SAL8667 500E LP in/out) | 1 pc Constant pressure valve CPV 3" DN80 (SAL9210 500E LP out) | 1 pc Pressure switche PP; digital output for inlet pressure monitoring (SAL9399 250E/500E LP in) | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out) | 1326
Note on X22: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: awaiting test results

## manual
SALINO® Pressure Center - Short Explanation to new Tool
Although Products and Physics didn`t change compared to former forms we decided to elaborate a new version of Design Tool:
1. General
1. One File fits to all Salino Models. You can choose within this file (see below) any of actual Salino model
2. All actual design parameters are updated. Use from now on just this file to avoid any hesitation
3. As an extra we added a feature to help you with the design of the right size of electrical motor
2. Inquiry Form - New
2.1 Main parameters are gathered in this sheet (and just there). This also a baseline of our quotation, so please handle with care
2.2 You can choose now directly between all existing Salino Models. Please consider that for the Salino 60 we have discrete types with individual Recovery- Rates.
2.3 Recovery Rates are available in certain steps. Any further Recovery-Rate shall be avoided resp. Must be clarified with Frankenthal
2.4 We make difference in pressure level (as before). Everything up to 70bar is standard. Between 70 and 120 bar please clarify application with Sales Team in Frankenthal
2.5 Exceptional Recovery Rates can be desfined by the use of the Offset on the Inquiry Form. Technical Feasibilty, delivery times and impact on costs has to be clairified with Salinnova Headquarter
3. Design Tool
3.1 As many parameters are gathered in the IQF you will find reduced input on this sheet
3.2 The design calculation are unchanged
3.3 We also show now the lubrication flow. We calculate the lubrication flow always to the nominal speed of the pump (1.500 RPMs)
3.4 You can "OPEN" and "CLOSE" the design feature for the electro-motor. Please use the buttons
3.5 We included recommendations for 2-; 4- and 6-pole motors (knowing that >75% will be 4-pole)
4. Flow Characteristic - NEW
4.1 This sheet shall explain the main conditions and characteristic of the designed Salino
4.2 This sheet is always specific to the design case
4.3 The graphics contents explanation to the graphs
4.4 The design reflects our central port plate. Following this logic shall help to explain our product.

## Inquiry Form
SALINO® Pressure Center ̶ Inquiry Form
[5 empty] | our Quotation / Order: |  | SalAG1XXX
| Our offer is based on following paramters: |  |  |  | rev: | 0 | date: | 2021-03-19
1. | Feed Water Quality | [5 empty] | = required Input
| Type |  | sea water
| Temperature | max. | 20 | °C
| Salinity | max. | 38000 | ppm
| Purity (Filter Qualiy) | < | 5 | µm
2. | RO Paramteres
| Feed Pressure to RO |  | 55 | bar
| Membran pressure drop |  | 1 | bar
| Permeate Flow |  | 5.4 | m³/h
| Selection | Salino | 250
| Number of SALINO®s required | information only | 1
| Feed Flow to RO |  | 15.4286 | m³/h
| Rotational speed |  | 1142.8571 | RPM
| Recovery Rate |  | 35 | %
| Offset RR |  | 0 | %
3. | Electrical Paramter
| Supply Line | Voltage | 400 | V
|  | Frequency | 50 | Hz
| Motor Start | Type | VFD
|  | Current | 120% | of nominal motor current (standard)
| www.salino.com |  | www.salinnova.com |  |  | engineered by:
| All values displayed are for information purposes only and do not represent guaranteed values. |  |  |  |  | Revision: |  | 200103_01_06

## Design Tool
SALINO® 250 Pressure Center ̶ Design Tool
[9 empty] | our Quotation/Order: |  | SalAG1XXX
[5 empty] | Recovery Rate |  |  |  | rev: | 0 | date: | 2021-03-19
[5 empty] | Recovery Rate | 35 | %
= required Input
Permeate
[9 empty] | Flow | 5.4 | m³/h
High Pressure Feed
| Flow | 15.4286 | m³/h | [5 empty] | Limiting Values for Operation
| Pressure | 55 | bar | [5 empty] | Minimum feed pressure |  |  | 3.8442 | bar
[9 empty] | Minimum operating pressure |  |  | 20 | bar
[9 empty] | Maximum operating pressure |  |  | 80 | bar
[5 empty] | High Pressure Brine |  |  |  | Minimum back pressure |  |  | 2.5 | bar
[5 empty] | Flow | 10.0286 | m³/h |  | Maximum water temperature |  |  | 50 | °C
[5 empty] | Pressure | 54 | bar |  | Minimum rotational speed |  |  | 600 | rpm
[9 empty] | Maximum rotational speed |  |  | 1750 | rpm
Input
[9 empty] | Permeate Flow |  |  | 129.6 | m³/day
[9 empty] | Membran pressure drop |  |  | 1 | bar
[9 empty] | Electric drive |  |  | Standard IE3 |  | electrical Supply
| Feed Water |  |  |  | Low Pressure Brine |  |  |  | Electrical Motor efficiency |  |  | 91.2 | % | Voltage: | 400 | V
| Flow | 16.0361 | m³/h |  | Flow | 9.5021 | m³/h |  | Frequency Converter |  |  | Standard |  | Freqency | 50 | Hz
| Min. pressure | 3.8442 | bar |  | Pressure | 3 | bar |  | Frequency Converter efficiency |  |  | 98 | % | safety mark-up | 12%
[9 empty] | SALINO® |  |  |  |  | ratio min | 55%
[9 empty] | SALINO® hydraulic efficiency |  |  | 97 | % | ratio max | 120%
[9 empty] | Number of SALINO®s required |  |  | 1
[9 empty] | Rotational speed |  |  | 1142.8571 | rpm | per pump unit:
| sea water |  |  |  | Total Lubrication Flow |  |  |  | Power savings |  |  | 13.0933 | kW | pole no. | 6 | 4
| Salinity | 38000 | ppm |  | Flow | 1.134 | m³/h |  | Total Lubrication Flow |  |  | 1.134 | m³/h | nominal speed | 986.6667 | 1480 | RPM
| Temperature | 20 | °C |  | max. pressure | 0.75 | bar |  | Energy Data |  |  |  |  | speed ratio (pump speed/nominal speed) | 115.8% | 77.22%
[9 empty] | Rated Power |  |  | 11.6926 | kW | min. nominal Motor power (incl. Mark-up) | 14.0942 | 16.959 | KW
[5 empty] | Warning |  |  |  | Energy costs |  |  | 0.11 | €/kWh | IE3 motor, nominal power | 15 | 18.5 | KW
[5 empty] | - none - |  |  |  | Energy efficiency |  |  | 2.1653 | kWh/m³ | IE3 motor, nominal efficiency | 91.73% | 92.23%
[9 empty] | est. Working hours per year |  |  | 8000.1576 | hrs./yr. | motor frame |  | 180M-4
| www.salino.com |  |  | www.salinnova.com |  |  |  |  | Energy savings |  |  | 117199.7923 | kWh/a | utilisation | 34.19% | 34.19%
| All values displayed are for information purposes only and do not represent guaranteed values. |  |  |  |  | engineered by: |  |  | CO2 savings |  |  | 70.9059 | t/a
[6 empty] | Revision: |  | 200103_01_06 | Energy cost savings |  |  | 12891.9772 | €/a

## Data Sheet (hidden)
SALINO® Pressure Center
Created: | 2021-03-20 |  | for RO-Desalination
SALINO® Design Tool |  |  | Project:
for prior membrane calculation
Limiting Values for Operation
|  | Minimum feed pressure: | #REF! | bar
|  | Minimum operating pressure: | 30 | bar
|  | Maximum operating pressure: | 80 | bar
|  | Minimum back pressure: | 2 | bar
|  | Maximum water temperature: | 50 | °C
Input from Calculation
|  | Feed TDS: | 38000 | ppm
|  | Overall Recovery: | 35 | %
|  | Permeate Flow: | 5.4 | m³/h
|  | (Membrane) Feed Pressure: | 55 | bar
|  | Feed Temperature: | 20 | °C
Operating Data (calculated)
|  | Number of SALINO®s required: | 1
|  | Feed water flow: | 16.0361 | m³/h
|  | Brine flow: | 9.5021 | m³/h
|  | Rotational speed: | 1142.8571 | rpm
|  | Membrane Pressure drop: | 1 | bar
|  | Energy costs: | 0.11 | €/kWh
SALINO® Pressure Center
|  | Manufactured in: | Duplex Stainless Steel
|  | Electrical Motor efficiency: | 91.2 | %
|  | Frequency Converter efficiency: | 98 | %
|  | Rated Power: | 11.6926 | kW
|  | Rated Maximum Power: | 15.2989 | kW
|  | Energy efficiency: | 2.1653 | kWh/m³
|  | CO2 savings: | 70.9059 | t/a
|  | Energy cost savings: | 12891.9772 | €/a
All calculated data presented does not represent guaranteed performance.

## Flow_Characteristic (hidden)
SALINO® 250 Pressure Center ̶ Flow Characteristic
55 | LP in | HP out | HP in | LP out
250 | SAE 2" | SAE 2" | SAE 2" | SAE 2"
Auxiliary Equipment:
A | HP Hoses | 0
B
C | LP Hoses | 0
D | CPV | 0
E | Sensor | 0
F |  | 4 pcs Pressure sensor PT; for operating in auto mode (SAL9245 LP in+out/HP in+out)
LP IN (Feed)
LP OUT (Drain)
HP OUT (to RO)
HP IN (from RO)
SAE 2"
SAE 2"
SAE 2"
SAE 2"

## Berechnungen (hidden)
Remark
Typ | 250 | 0 |  | SALINO® | Pressure Center ̶ Design Tool |  | Pressure Center ̶ Flow Characteristic
SALINO® 250 Pressure Center ̶ Design Tool
Berechnungen |  |  |  | SALINO® 250 Pressure Center ̶ Flow Characteristic
Input | Recovery Rate | RR | 35 | % |  | gegeben | Volume pump | Vpump | 225 | cm3
| Membrane Feed Pressure | ps | 55 | bar |  |  | mechanical efficiency | ηmech | 96 | %
| Maximum operating pressure | ps max | 80 | bar |  |  | volumetric efficiency pump | ηvol pump | 97 | %
| Permeate Flow | Qperm | 5.4 | m3/h |  |  | volumetric efficiency motor | ηvol motor | 96 | %
|  |  | 129.6 | m3/d |  |  | CO2 equivalent | mCO2/kWh | 0.605 | kg/kWh
| Feed Temperature | Tfeed | 20 | °C
| Feed Salinity | Sfeed | 38000 | ppm
| Membrane Pressure Drop | Δpv | 1 | bar
| Brine discharge pressure | pback | 3 | bar
| Electrical Motor efficiency | ηEM | 91.2 | %
| Frequency Converter efficiency | ηFU | 98 | %
| Energy Costs | KE | 0.11 | €/kWh
| Front pressure | pfeed lp | 3.8442 | bar
= erforderliche Eingabe
[7 empty] | Max. Membrane Pressure ps max | 80 | bar
| Feed High Pressure | Qfeed hp | 15.4286 | m3/h |  |  |  | 15.4286 | m3/h
| Brine High Pressure | Qbrine hp | 10.0286 | m3/h |  |  |  | 10.0286 | m3/h
| Feed Low Pressure | Qfeed lp | 16.0361 | m3/h |  |  |  | 15.9057 | m3/h
| Brine Low Pressure | Qbrine lp | 9.5021 | m3/h |  |  |  | 9.6274 | m3/h
| Total Lubrication Flow | Qlub | 1.134 | m3/h |  |  |  | 0.87832 | m3/h
| calculated Rotational speed | n | 1142.8571 | rpm |  |  |  | 1142.8571 | rpm
| Rotational speed per SALINO | n | 1142.8571 | rpm |  |  |  | 1142.8571 | rpm
| difference pressure pump | dp | 51.1558 | bar |  |  |  | 76.1558 | bar
| Brine High Pressure | pbrine hp | 54 | bar |  |  |  | 79 | bar
| Power Pump | Ppump | 23.5437 | kW |  |  |  | 33.9981 | kW
| Volume ERD | VERD | 146.25 | cm3 |  |  |  | 146.25 | cm3
| Power ERD | PERD | 13.0933 | kW | uptime | 91.33% |  | 20.3246 | kW
| Power shaft | Pshaft | 10.4504 | kW | hours/years | 8000.1576 |  | 13.6735 | kW
| Electrical Power | Pel | 11.6926 | kW |  |  |  | 15.2989 | kW
| Energy efficiency | SECel | 2.1653 | kWh/m3 |  |  |  | 2.8331 | kWh/m3
| specific Energy Costs | KE spec | 0.23818 | €/m3 |  |  |  | 0.31164 | €/m3
| Energy savings | Esave el/a | 117199.7923 | kWh/a | 104748.4864 |  |  | 199206.9971 | kWh/a
| CO2 savings | CO2 saving/a | 70.9059 | t/a |  |  |  | 120.5202 | t/a
| Energy cost savings | KE save/a | 12891.9772 | €/a |  |  |  | 21912.7697 | €/a
= wird dem Kunden angezeigt
[7 empty] | min. pressure switch off (Kidney) | 3 | bar
[7 empty] | delta p max. speed | -3.3 | bar
[7 empty] | warning | 0.1
[7 empty] | factor a | 0.15
| angebotene RR | 25 | % | Maximum operating pressure
1 |  | 30 | % |  | 80 | bar | Minimum feed pressure f(n) | 3.8442 | bar
2 |  | 35 | % |  | 120 | bar
3 |  | 40 | % |  |  |  | Rotational speed | 600 | 791.6667 | 983.3333 | 1175 | 1366.6667 | 1558.3333 | 1750
4 |  | 45 | % | Anzahl notw. SALINOs |  | 1 | min. pressure (bar); switch off (Kidney) | 3 | 3 | 3 | 3 | 3 | 3 | 3
5 |  | 50 | % |  |  |  | warning pressure (bar); alarm (Kidney) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
6 |  | 55 | % |  |  |  | Minimum feed pressure (bar) | 3.45 | 3.5611 | 3.7029 | 3.8753 | 4.0782 | 4.3118 | 4.576
7 |  |  |  | Warning | 1
8
9
10 |  |  |  |  | SALINO®
SALINO® 250
Pressure Center pressure limits Feed side
| Feed water Type | sea water |  |  | SALINO® 250 Pressure Center pressure limits Feed side
brackish water
landfill leachate
others (must bespecified)
HP Out
|  | pmin | 20
|  | pmax1 | 80
|  | pmax2 | 120
LP Out
|  | pmin | 2.5
|  | pmax | 4
[7 empty] | Rotational speed | 600 | 791.6667 | 983.3333 | 1175 | 1366.6667 | 1558.3333 | 1750 | 1142.8571 | RPMs | Faktor | 600 | 791.6667 | 983.3333 | 1175 | 1366.6667 | 1558.3333 | 1750 | RPMs
max. salinity | 50000 | Minimum water temperature | 2 |  | pump flow ( | :1 m³/hr per unit) | pump flow (5:1 m³/hr per unit) | 40.5 | 53.4375 | 66.375 | 79.3125 | 92.25 | 105.1875 | 118.125 | 77.1429 | m³/hr | 5 | 8.1 | 10.6875 | 13.275 | 15.8625 | 18.45 | 21.0375 | 23.625 | m³/hr
|  | Maximum water temperature | 50 |  |  |  | pressure range standard application (bar) | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | bar |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | bar
|  | Minimum rotational speed | 600 |  |  |  | pressure range to be confirmed individual (bar) | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | bar |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | bar
|  | Maximum rotational speed | 1750 |  |  | design case | design caseSALINO® 250 RR 35% @ 55 bar [5:1 KW per unit] | [7 empty] | 58.4632
|  | RR | 35 | % @ | 55 | bar shaft-power demand [ | RR 35% @ 55 bar shaft-power demand [5:1 KW per unit] | 30.6932 | 40.4979 | 50.3027 | 60.1075 | 69.9122 | 79.717 | 89.5218 |  | KW |  | 6.1386 | 8.0996 | 10.0605 | 12.0215 | 13.9824 | 15.9434 | 17.9044 | KW
lubrication/leakage lines
|  | pmax | 0.75
SALINO® 250
| Motoren | Standard IE3
|  | Non-Standard |  |  | Pressure Center performance range HP OUT
bare shaft pump
SALINO® 250 Pressure Center performance range HP OUT
| FU | Standard
Non-Standard
exclusive
HP In
SALINO® 250
Pressure Center criterias HP IN
SALINO® 250 Pressure Center criterias HP IN
[5 empty] | LP OUT |  | - back-pressure range between | - back-pressure range between 2,5 and 4 bar
SALINO® 250
Pressure Center criterias LP Out
SALINO® 250 Pressure Center criterias LP Out
Motor
[6 empty] | 90 | Rotational speed | 600 | 791.6667 | 983.3333 | 1175 | 1366.6667 | 1558.3333 | 1750 |  | RPMs
[7 empty] | pump flow (m³/hr) | 8.1 | 10.6875 | 13.275 | 15.8625 | 18.45 | 21.0375 | 23.625 |  | m³/hr
|  | RR | 25 | % @ | 80 | bar shaft-power demand [KW] | RR 25% @ 80 bar shaft-power demand [KW] | 4.905 | 6.4719 | 8.0387 | 9.6056 | 11.1725 | 12.7394 | 14.3062 |  | KW
|  | RR | 40 | % @ | 80 | bar shaft-power demand [KW] | RR 40% @ 80 bar shaft-power demand [KW] | 7.848 | 10.355 | 12.862 | 15.369 | 17.876 | 20.383 | 22.89 |  | KW
|  | RR | 55 | % @ | 80 | bar shaft-power demand [KW] | RR 55% @ 80 bar shaft-power demand [KW] | 10.791 | 14.2381 | 17.6852 | 21.1324 | 24.5795 | 28.0266 | 31.4737 |  | KW
|  | RR | 75 | % @ | 80 | bar shaft-power demand [KW] | RR 75% @ 80 bar shaft-power demand [KW] | 14.715 | 19.4156 | 24.1163 | 28.8169 | 33.5175 | 38.2181 | 42.9187 |  | KW
SALINO® 250
shaft-power demand [KW]
shaft-power demand [KW]

## Units (hidden)
Unit Selection
Umrechnungsfaktoren
pressure | TRUE | 1 | bar | 1
| FALSE | 14.5038 | psi
flow | TRUE | 1 | m³/h | 1
| FALSE | 4.4029 | gpm
temperature | TRUE
FALSE

## IE3 Motoren (hidden)
|  | Nennleistung | IE1 Standard Wirkungsgrad |  |  | IE2 Hoher Wirkungsgrad |  |  | IE3 Premium Wirkungsgrad
|  | kW | 2-polig | 4-polig | 6-polig | 2-polig | 4-polig | 6-polig | 2-polig | 4-polig | 6-polig | minimum
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
0.75 | 80M-4 | 0.75 | 72.1% | 72.1% | 70% | 77.4% | 79.6% | 75.9% | 80.7% | 82.5% | 78.9% | 0.807 |  | 78%
1.1 | 90S-4 | 1.1 | 75% | 75% | 72.9% | 79.6% | 81.4% | 78.1% | 82.7% | 84.1% | 81% | 0.826 |  | 81%
1.5 | 90L-4 | 1.5 | 77.2% | 77.2% | 75.2% | 81.3% | 82.8% | 79.8% | 84.2% | 85.3% | 82.5% | 0.84 |  | 82%
2.5 | 90L-4V* | 2.5 | 79.7% | 79.7% | 77.7% | 83.2% | 84.3% | 81.8% | 85.9% | 86.7% | 84.3% | 0.85633 |  | 84%
3 | 100L-4 | 3 | 81.5% | 81.5% | 79.7% | 84.6% | 85.5% | 83.3% | 87.1% | 87.7% | 85.6% | 0.868 |  | 85%
4 | 112M-4 | 4 | 83.1% | 83.1% | 81.4% | 85.8% | 86.6% | 84.6% | 88.1% | 88.6% | 86.8% | 0.87833 |  | 86%
5.5 | 132S-4 | 5.5 | 84.7% | 84.7% | 83.1% | 87% | 87.7% | 86% | 89.2% | 89.6% | 88% | 0.88933 |  | 88%
7.5 | 132M-4 | 7.5 | 86% | 86% | 84.7% | 88.1% | 88.7% | 87.2% | 90.1% | 90.4% | 89.1% | 0.89867 |  | 89%
11 | 160M-4 | 11 | 87.6% | 87.6% | 86.4% | 89.4% | 89.8% | 88.7% | 91.2% | 91.4% | 90.3% | 0.90967 |  | 90%
15 | 160L-4 | 15 | 88.7% | 88.7% | 87.7% | 90.3% | 90.6% | 89.7% | 91.9% | 92.1% | 91.2% | 0.91733 |  | 91%
18.5 | 180M-4 | 18.5 | 89.3% | 89.3% | 88.6% | 90.9% | 91.2% | 90.4% | 92.4% | 92.6% | 91.7% | 0.92233 |  | 91%
22 | 180L-4 | 22 | 89.9% | 89.9% | 89.2% | 91.3% | 91.6% | 90.9% | 92.7% | 93% | 92.2% | 0.92633 |  | 92%
30 | 200L-4K | 30 | 90.7% | 90.7% | 90.2% | 92% | 92.3% | 91.7% | 93.3% | 93.6% | 92.9% | 0.93267 |  | 92%
37 | 225S-4 | 37 | 91.2% | 91.2% | 90.8% | 92.5% | 92.7% | 92.2% | 93.7% | 93.9% | 93.3% | 0.93633 |  | 93%
45 | 225M-4 | 45 | 91.7% | 91.7% | 91.4% | 92.9% | 93.1% | 92.7% | 94% | 94.2% | 93.7% | 0.93967 |  | 93%
55 | 250M-4 | 55 | 92.1% | 92.1% | 91.9% | 93.2% | 93.5% | 93.1% | 94.3% | 94.6% | 94.1% | 0.94333 |  | 94%
75 | 280S-4 | 75 | 92.7% | 92.7% | 92.6% | 93.8% | 94% | 93.7% | 94.7% | 95% | 94.6% | 0.94767 |  | 94%
90 | 280M-4K | 90 | 93% | 93% | 92.9% | 94.1% | 94.2% | 94% | 95% | 95.2% | 94.9% | 0.95033 |  | 94%
110 | 315S-4 | 110 | 93.3% | 93.3% | 93.3% | 94.3% | 94.5% | 94.3% | 95.2% | 95.4% | 95.1% | 0.95233 |  | 95%
132 | 315M-4 | 132 | 93.5% | 93.5% | 93.5% | 94.6% | 94.7% | 94.6% | 95.4% | 95.6% | 95.4% | 0.95467 |  | 95%
160 | 315L-4K | 160 | 93.8% | 93.8% | 93.8% | 94.8% | 94.9% | 94.8% | 95.6% | 95.8% | 95.6% | 0.95667 |  | 95%
200 | 315L-4M | 200 | 94% | 94% | 94% | 95% | 95.1% | 95% | 95.8% | 96% | 95.8% | 0.95867 |  | 95%
250 | 315L-4L* | 250 | 94% | 94% | 94% | 95% | 95.1% | 95% | 95.8% | 96% | 95.8% | 0.95867 |  | 95%
315 | 315L-4V* | 315 | 94% | 94% | 94% | 95% | 95.1% | 95% | 95.8% | 96% | 95.8% | 0.95867 |  | 95%
|  | 355 | 94% | 94% | 94% | 95% | 95.1% | 95% | 95.8% | 96% | 95.8% | 0.95867
|  | 375 | 94% | 94% | 94% | 95% | 95.1% | 95% | 95.8% | 96% | 95.8% | 0.95867
|  | 78% | 81% | 82% | 84% | 85% | 86% | 88% | 89% | 90% | 91% | 91% | 92% | 92% | 93% | 93% | 94% | 94% | 94% | 95% | 95% | 95% | 95% | 95% | 95%

## Quotation data (hidden)
SALINO® 500 Pressure Center scope of supply
Item | Description | Part no. | Qty. | Unit
00100 | 64075035 |  | 1 | PC
SALINO Pressure Center
Material: Duplex 1.4462
Recovery Rate 35 %
00110 | MAT.-NR. 75 kW Motor |  | 1 | PC
Squirrel-Cage-Motor
Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B)
IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz)
3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD
Frame material: grey cast iron
paint finish resistant to salt-laden air
motor protection 3 PTC thermistors
00120 | 01554711 |  | 1 | PC
Bellhousing PG550
00130 | 01554712 |  | 1 | PC
Flexible Coupling Bowex I 80
00140 | 01553741 |  | 1 | PC
Mountingframe 270x600x2075
00200 | MAT.-NR. Pumpdrive R 75 kW |  | 1 | PC
Frequency Converter PumpDrive R (KSB202)
3AC 380-480 V ±10 % * 50/60 Hz
IP20 * 75 kW * I at 400V=61,0A
Maximum ambient temperature +50°C
Dimensions [mm] H=650 x B=242 x T=260

## Identnumbers (hidden)
Recovery Rate | bare shaft pump | PC 33 (55 kW) | PC 64 (75 kW) | Non-Standard
25 | 10625025 | 33055025 | 64075025 | 00025
26 | 10625026 | 33055026 | 64075026 | 00026
27 | 10625027 | 33055027 | 64075027 | 00027
28 | 10625028 | 33055028 | 64075028 | 00028
29 | 10625029 | 33055029 | 64075029 | 00029
30 | 10625030 | 33055030 | 64075030 | 00030
31 | 10625031 | 33055031 | 64075031 | 00031
32 | 10625032 | 33055032 | 64075032 | 00032
33 | 10625033 | 33055033 | 64075033 | 00033
34 | 10625034 | 33055034 | 64075034 | 00034
35 | 10625035 | 33055035 | 64075035 | 00035
36 | 10625036 | 33055036 | 64075036 | 00036
37 | 10625037 | 33055037 | 64075037 | 00037
38 | 10625038 | 33055038 | 64075038 | 00038
39 | 10625039 | 33055039 | 64075039 | 00039
40 | 10625040 | 33055040 | 64075040 | 00040
41 | 10625041 | 33055041 | 64075041 | 00041
42 | 10625042 | 33055042 | 64075042 | 00042
43 | 10625043 | 33055043 | 64075043 | 00043
44 | 10625044 | 33055044 | 64075044 | 00044
45 | 10625045 | 33055045 | 64075045 | 00045
46 | 10625046 | 33055046 | 64075046 | 00046
47 | 10625047 | 33055047 | 64075047 | 00047
48 | 10625048 | 33055048 | 64075048 | 00048
49 | 10625049 | 33055049 | 64075049 | 00049
50 | 10625050 | 33055050 | 64075050 | 00050
55 | 10625051 | 33055051 | 64075051 | 00051
75 | 10625052 | 33055052 | 64075052 | 00052
Spaltenindex | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| Mat.-Nr. | Motor Mat.-Nr. | Motorbezeichnung | Motordaten Zeile 1 | Motordaten Zeile 2 | Motordaten Zeile 3 | Motordaten Zeile 4 | Motordaten Zeile 5 | Motordaten Zeile 6 | Mat.-Nr. Pumpenträger | Pumpenträgerbezeichnung | Mat.-Nr. Kupplung | Kupplungsbezeichnung | Mat.-Nr. Montagerahmen | Montagerahmenbezeichnung | FU-Mat.-Nr. | FU-Bezeichnung | FU-Daten Zeile 1 | FU-Daten Zeile 2 | FU-Daten Zeile 3 | FU-Daten Zeile 4
barshaft pump | 10625025
10625026
10625027
10625028
10625029
10625030
10625031
10625032
10625033
10625034
10625035
10625036
10625037
10625038
10625039
10625040
10625041
10625042
10625043
10625044
10625045
10625046
10625047
10625048
10625049
10625050
10625051
10625052
PC 33 | 33055025 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553705 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055026 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553706 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055027 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553707 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055028 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553708 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055029 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553709 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055030 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553710 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055031 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553711 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055032 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553712 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055033 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553713 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055034 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553714 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055035 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553715 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055036 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553716 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055037 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553717 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055038 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553718 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055039 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553719 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055040 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553720 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055041 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553721 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055042 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553722 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055043 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553723 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055044 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553724 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055045 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553725 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055046 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553726 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055047 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553727 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055048 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553728 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055049 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553729 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055050 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553730 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055051 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553730 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 33055052 | MAT.-NR. 55 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG250M * IMB35 * 55kW (50 Hz) * 66kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553731 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 55 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 55 kW * I at 400V=44,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
PC 64 | 64075025 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553731 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075026 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553732 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075027 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553733 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075028 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553734 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075029 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553735 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075030 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553736 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075031 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553737 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075032 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553738 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075033 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553739 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075034 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553740 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075035 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553741 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075036 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553742 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075037 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553743 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075038 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553744 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075039 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553745 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075040 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553746 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075041 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553747 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075042 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553748 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075043 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553749 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075044 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553750 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075045 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553751 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075046 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553752 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075047 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553753 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075048 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553754 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075049 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553755 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075050 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553756 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075051 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553756 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
| 64075052 | MAT.-NR. 75 kW Motor | Squirrel-Cage-Motor | Premium Efficiency IE3; self ventilated; Isulation 155(F) to 130(B) | IP55 * 4pole * BG280S * IMB35 * 75kW (50 Hz) * 90kW (60Hz) | 3 AC 50Hz 400VD/690VY * 3 AC 60Hz 460VD | Frame material: grey cast iron | paint finish resistant to salt-laden air | motor protection 3 PTC thermistors | 01554711 | Bellhousing PG550 | 01554712 | Flexible Coupling Bowex I 80 | 01553756 | Mountingframe 270x600x2075 | MAT.-NR. Pumpdrive R 75 kW | Frequency Converter PumpDrive R (KSB202) | 3AC 380-480 V ±10 % * 50/60 Hz | IP20 * 75 kW * I at 400V=61,0A | Maximum ambient temperature +50°C | Dimensions [mm] H=650 x B=242 x T=260
Non-Standard Motor | 00025 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00026 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00027 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00028 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00029 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00030 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00031 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00032 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00033 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00034 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00035 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00036 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00037 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00038 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00039 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00040 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00041 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00042 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00043 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00044 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00045 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00046 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00047 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00048 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00049 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
| 00050 | Electric motor according to customers specification
| 00051 | Electric motor according to customers specification
| 00052 | Electric motor according to customers specification | [7 empty] | Bellhousing according to motor dimensions |  | Flexible Coupling according to motor dimensions |  | Mountingframe according to motor dimensions |  | Frequency Converter according customers specification
non-standard FU |  | Frequency Converter according to customers specification